Climate Resilience Measures for Water Supply in Jeju Province South Korea

Jinkeun Kim*

*Dept. of Environmental Engineering, Jeju National University, Jeju 63243, Republic of Korea, kjinkeun@jejunu.ac.kr

Abstract: Climate change adaptation strategies for 16 water treatment plants (WTPs) in Jeju Province were investigated. Drought, heat wave, and heavy rain were among the most critical climate factors affecting water utilities of Jeju Province in South Korea.

Reduction of non-revenue water (NRW) and water use have been proposed as adaptation measures for drought. On the other hand, the introduction of an advanced water treatment process and the installation of an automatic coagulant injection device were proposed as adaptation measures for heat waves and heavy rains, respectively.

Keywords: Climate change; adaptation strategy; water supply system

Introduction

Climate change due to excessive carbon dioxide emissions is causing abnormal climate phenomena such as heat wave, heavy rain, and drought in water supply facilities. Water supply facilities need to evaluate the risks of climate change in preparation for such extreme climate occurrences and establish climate change adaptation measures to reduce its risks. This study presents cases of establishing climate crisis adaptation measures for 16 WTPs in Jeju Province South Korea.

Materials and Methods

Jeju Province operates 16 WTPs (total capacity: 357,000 m3/day). Nine of these WTPs only carry out chlorine disinfection and supply water after intake at a depth of 100-300 m underground, and six WTPs supply water after a slow or rapid filtration process using river or spring water. Only one WTP takes lake water as raw water.

The climate change risk assessments for WTPs were implemented as the product of the possibility and impact of extreme weather. The occurrence possibility of extreme climate factors was presented by the government, and the degree of impact was calculated based on the results of a survey done by water facility workers. The survey was conducted using a checklist that was subdivided into facilities,

Results and Discussion

Based on the climate change risk assessment of 16 WTPs in Jeju, the most severe climate crises were identified in the order of drought, heat wave, and heavy rain, and adaptation measures were established for each.

A. Adaptation strategy for drought

Drought means a decrease in tap water supply capacity. To solve this problem, Jeju Province plans to increase the revenue water ratio from 54.2% as of 2023 to 85% by 2035. Efforts are also needed to expand and distribute water-saving devices and expand the installation of water reuse facilities to continuously reduce 335.9 liter per capita day (lpcd), which exceeds about 10.5% of the nation's average water use (303.9 lpcd). Figure 1.1 shows lpcd status in Korea and Jeju Province.

Figure 1.1 Lpcd of national average and Jeju.         Figure 1.2 Algae concentration at E lake.

B. Adaptation strategy for heat wave

The possible effects of the heat wave on the water supply are an increase of algae concentration which can cause color as well as taste and odor in tap water, requires the introduction of an advanced water purification process consisting of ozone oxidation and granular activated carbon adsorption process. Figure 1.2 shows the algae concentration of E lake.

C. Adaptation strategy for heavy rain

Jeju Province is a volcanic island with high water permeability, so the development of river is relatively weak. River water depends on most of the spring water, and during heavy rain, the turbidity spike of the spring and river water has been observed. Most surface WTPs in Jeju Province have filtration facilities, but when the turbidity of raw water exceeds 2 NTU, most of them stop treating raw water and respond to an increase in the production of nearby WTPs that intake groundwater. Therefore, it is desirable to install an automatic coagulant injection instrument in front of the filtration facility and perform water treatment continuously even under heavy rain.

Conclusions

Based on climate change risk assessment on 16 WTPs in Jeju, several adaptation measures were recommended.

The most essential adaptation strategy for drought is to reduce the leakage rate. In addition, efforts are needed to reduce water consumption which is constantly increasing. As an adaptation measure to the heat wave, it is necessary to install an advanced water purification process to reduce the concentration of taste and odor substances caused by algae. The installation and operation of an automatic coagulant injection device can reduce risk of turbidity spike in raw water caused by heavy rain.

REFERENCES

AWWA, 2021 Climate Action Plans-Adaptive Management Strategies for Utilities.

Jeju Province, 2023 Report on Climate Crisis Adaptation Strategies for Jeju WTPs.